Taronga Zoo holds an Environment Protection Licence (EPL #: 1677) to discharge water into Sydney Harbour. This licence is issued under the Protection of the Environment Operations Act 1997 (POEO Act).

In accordance with section 66(6) of the Act Taronga is required to publish pollution monitoring results gathered as a result of Taronga’s Recycled Treatment Plant operation.  The intention of this requirement is to improve the general public’s access to information about the environmental performance of licensed facilities.

| Organisation | Taronga Conservation Society Australia |
| --- | --- |
| Site | Taronga Zoo |
| Address | Bradleys Head Road Mosman, NSW 2088 |
| Activity | Taronga Recycled Water Treatment Plant |
| EPL Number | 1677 |
| Web link | Taronga EPL 1677 Details |

| Date sampled | 20 March 2012 |
| --- | --- |
| Results received | 4 April 2012 |
| Results Published | 4 July 2012 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8.1 | - | - |
|  |  | TSS | <3 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.8 | 6.5-8.5 | - |
|  |  | TSS | 4 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 17 April 2012 |
| --- | --- |
| Results received | 2 May 2012 |
| Results Published | 4 July 2012 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8.1 | - | - |
|  |  | TSS | 4 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.7 | 6.5-8.5 | - |
|  |  | TSS | 4 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 13 May 2012 |
| --- | --- |
| Results received | 30 May 2012 |
| Results Published | 4 July 2012 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 7.8 | - | - |
|  |  | TSS | <3 | 50 | mg/L |
|  |  | BOD | <4 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.7 | 6.5-8.5 | - |
|  |  | TSS | 8 | 20 | mg/L |
|  |  | BOD | <4 | 15 | mg/L |

| Date sampled | 7 June 2012 |
| --- | --- |
| Results received | 19 June 2012 |
| Results Published | 4 July 2012 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 7.9 | - | - |
|  |  | TSS | <2 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.7 | 6.5-8.5 | - |
|  |  | TSS | 11 | 20 | mg/L |
|  |  | BOD | 4 | 15 | mg/L |

| Date sampled | 25 July 2012 |
| --- | --- |
| Results received | 3 August 2012 |
| Results Published | 13 August 2012 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8 | - | - |
|  |  | TSS | 3 | 50 | mg/L |
|  |  | BOD | 4 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.5 | 6.5-8.5 | - |
|  |  | TSS | 12 | 20 | mg/L |
|  |  | BOD | 3 | 15 | mg/L |

| Date sampled | 16 August 2012 |
| --- | --- |
| Results received | 28 August 2012 |
| Results Published | 27 September 2012 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 7.9 | - | - |
|  |  | TSS | 3 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.3 | 6.5-8.5 | - |
|  |  | TSS | 14 | 20 | mg/L |
|  |  | BOD | 4 | 15 | mg/L |

| Date sampled | 6 September 2012 |
| --- | --- |
| Results received | 14 September 2012 |
| Results Published | 27 September 2012 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8.1 | - | - |
|  |  | TSS | 8 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.6 | 6.5-8.5 | - |
|  |  | TSS | <3 | 20 | mg/L |
|  |  | BOD | 8 | 15 | mg/L |

| Date sampled | 12 October 2012 |
| --- | --- |
| Results received | 19 October 2012 |
| Results Published | 23 October 2012 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 7.9 | - | - |
|  |  | TSS | 4 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.6 | 6.5-8.5 | - |
|  |  | TSS | 8 | 20 | mg/L |
|  |  | BOD | 3 | 15 | mg/L |

| Date sampled | 14 November2012 |
| --- | --- |
| Results received | 28 November 2012 |
| Results Published | 4 December 2012 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8 | - | - |
|  |  | TSS | 4 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.6 | 6.5-8.5 | - |
|  |  | TSS | 5 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 6 December 2012 |
| --- | --- |
| Results received | 18 December 2012 |
| Results Published | 20 December 2012 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8.1 | - | - |
|  |  | TSS | 4 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.8 | 6.5-8.5 | - |
|  |  | TSS | 6 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 11 January 2013 |
| --- | --- |
| Results received | 22 January 2013 |
| Results Published | 4 February 2013 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8.1 | - | - |
|  |  | TSS | 20 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.8 | 6.5-8.5 | - |
|  |  | TSS | <3 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 7 February 2013 |
| --- | --- |
| Results received | 18 February 2013 |
| Results Published | 20 February 2013 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8 | - | - |
|  |  | TSS | 34 | 50 | mg/L |
|  |  | BOD | 4 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.4 | 6.5-8.5 | - |
|  |  | TSS | 4 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 31 March 2013 |
| --- | --- |
| Results received | 3 April 2013 |
| Results Published | 17 May 2013 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 7.8 | - | - |
|  |  | TSS | 75 | 50 | mg/L |
|  |  | BOD | 3 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.6 | 6.5-8.5 | - |
|  |  | TSS | 6 | 20 | mg/L |
|  |  | BOD | 5 | 15 | mg/L |

| Date sampled | 24 April 2013 |
| --- | --- |
| Results received | 3 May 2013 |
| Results Published | 17 May 2013 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 7.9 | - | - |
|  |  | TSS | 37 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.6 | 6.5-8.5 | - |
|  |  | TSS | 6 | 20 | mg/L |
|  |  | BOD | 5 | 15 | mg/L |

| Date sampled | 10 May 2013 |
| --- | --- |
| Results received | 16 May 2013 |
| Results Published | 17 May 2013 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 7.9 | - | - |
|  |  | TSS | 42 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.9 | 6.5-8.5 | - |
|  |  | TSS | 39* LRE | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 17 June |
| --- | --- |
| Results received | 27 June 2013 |
| Results Published | 9 July 2013 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 7.9 | - | - |
|  |  | TSS | 17 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.6 | 6.5-8.5 | - |
|  |  | TSS | 4 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 26 July |
| --- | --- |
| Results received | 16 August 2013 |
| Results Published | 2 Sept 2013 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 7.9 | - | - |
|  |  | TSS | 10 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.7 | 6.5-8.5 | - |
|  |  | TSS | <2 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 21 Aug 2013 |
| --- | --- |
| Results received | 2 Sept 2013 |
| Results Published | 9 Sept 2013 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 7.9 | - | - |
|  |  | TSS | 5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.6 | 6.5-8.5 | - |
|  |  | TSS | 5 | 20 | mg/L |
|  |  | BOD | 3 | 15 | mg/L |

| Date sampled | 12 Sept 2013 |
| --- | --- |
| Results received | 23 Sept 2013 |
| Results Published |  |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8.1 | - | - |
|  |  | TSS | 4 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.5 | 6.5-8.5 | - |
|  |  | TSS | 5 | 20 | mg/L |
|  |  | BOD | 11 | 15 | mg/L |

| Date sampled | 24 October 2013 |
| --- | --- |
| Results received | 1 November 2013 |
| Results Published |  |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8.1 | - | - |
|  |  | TSS | <2 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.7 | 6.5-8.5 | - |
|  |  | TSS | <2 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 29 November 2013 |
| --- | --- |
| Results received | 9 December 2013 |
| Results Published |  |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8.1 | - | - |
|  |  | TSS | <2 | 50 | mg/L |
|  |  | BOD | 3 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.8 | 6.5-8.5 | - |
|  |  | TSS | <2 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 16 December 2013 |
| --- | --- |
| Results received | 30 December 2013 |
| Results Published |  |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8 | - | - |
|  |  | TSS | <2 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.6 | 6.5-8.5 | - |
|  |  | TSS | <2 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 9 January 2014 |
| --- | --- |
| Results received | 17 January 2014 |
| Results Published |  |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 7.6 | - | - |
|  |  | TSS | 3 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 8.1 | 6.5-8.5 | - |
|  |  | TSS | 4 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 7 February 2014 |
| --- | --- |
| Results received | 18 February 2014 |
| Results Published |  |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8.1 | - | - |
|  |  | TSS | 4 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.5 | 6.5-8.5 | - |
|  |  | TSS | <2 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 14 March 2014 |
| --- | --- |
| Results received | 21 March 2014 |
| Results Published | 23 March 2014 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8.1 | - | - |
|  |  | TSS | <2 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.3 | 6.5-8.5 | - |
|  |  | TSS | <2 | 20 | mg/L |
|  |  | BOD | 4 | 3 | mg/L |

| Date sampled | 3 April |
| --- | --- |
| Results received | 20 May |
| Results Published | 23 May |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8 | - | - |
|  |  | TSS | 6 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.6 | 6.5-8.5 | - |
|  |  | TSS | 8 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 9 May 2014 |
| --- | --- |
| Results received | 21 May 2014 |
| Results Published | 23 May 2014 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8 | - | - |
|  |  | TSS | 4 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.4 | 6.5-8.5 | - |
|  |  | TSS | 8 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 5 June 2014 |
| --- | --- |
| Results received | 17 June 2014 |
| Results Published | 23 June 2014 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8 | - | - |
|  |  | TSS | 5 | 50 | mg/L |
|  |  | BOD | 4 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.6 | 6.5-8.5 | - |
|  |  | TSS | 13 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 11 July 2014 |
| --- | --- |
| Results received | 20 July 2014 |
| Results Published | 28 July 2014 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8 | - | - |
|  |  | TSS | 4 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.5 | 6.5-8.5 | - |
|  |  | TSS | 6 | 20 | mg/L |
|  |  | BOD | 5 | 15 | mg/L |

| Date sampled | 7 August 2014 |
| --- | --- |
| Results received | 19 August 2014 |
| Results Published | 22 August 2014 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8.1 | - | - |
|  |  | TSS | <2 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.4 | 6.5-8.5 | - |
|  |  | TSS | 6 | 20 | mg/L |
|  |  | BOD | 22 | 15 | mg/L |

| Date sampled | 18 September 2014 |
| --- | --- |
| Results received | 26 September 2014 |
| Results Published | 26 September 2014 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8 | - | - |
|  |  | TSS | <2 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.3 | 6.5-8.5 | - |
|  |  | TSS | 2 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 9 October 2014 |
| --- | --- |
| Results received | 22 October 2014 |
| Results Published | 27 October 2014 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8 | - | - |
|  |  | TSS | <2 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.4 | 6.5-8.5 | - |
|  |  | TSS | 2 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 13 November 2014 |
| --- | --- |
| Results received | 25 November 2014 |
| Results Published | 28 November 2014 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 8.1 | - | - |
|  |  | TSS | 4 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.6 | 6.5-8.5 | - |
|  |  | TSS | <2 | 20 | mg/L |
|  |  | BOD | 4 | 15 | mg/L |

| Date sampled | 5th December 2014 |
| --- | --- |
| Results received | 16th December 2014 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 1 | Monthly frequency | pH | 7.9 | - | - |
|  |  | TSS | 7 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 2 | Monthly frequency | pH | 7.4 | 6.5-8.5 | - |
|  |  | TSS | 9 | 20 | mg/L |
|  |  | BOD | 5 | 15 | mg/L |

| Date sampled | 22 January 2015 |
| --- | --- |
| Results received | 22 January 2015 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.9 | - | - |
|  |  | TSS | 11 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.3 | 6.5-8.5 | - |
|  |  | TSS | <2 | 20 | mg/L |
|  |  | BOD | 3 | 15 | mg/L |

| Date sampled | 12 March 2015 |
| --- | --- |
| Results received | 20 March 2015 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8 | - | - |
|  |  | TSS | 10 | 50 | mg/L |
|  |  | BOD | 3 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.7 | 6.5-8.5 | - |
|  |  | TSS | <2 | 20 | mg/L |
|  |  | BOD | 4 | 15 | mg/L |

| Date sampled | 27 March 2015 |
| --- | --- |
| Results received | 2 April 2015 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8 | - | - |
|  |  | TSS | 3 | 50 | mg/L |
|  |  | BOD | 2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.6 | 6.5-8.5 | - |
|  |  | TSS | 8 | 20 | mg/L |
|  |  | BOD | 7 | 15 | mg/L |

| Date sampled | 16 April 2015 |
| --- | --- |
| Results received | 24 April 2015 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.9 | - | - |
|  |  | TSS | 4 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.5 | 6.5-8.5 | - |
|  |  | TSS | 3 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 15 May 2015 |
| --- | --- |
| Results received | 25 May 2015 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8 | - | - |
|  |  | TSS | 8 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.8 | 6.5-8.5 | - |
|  |  | TSS | 3 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 15 May 2015 |
| --- | --- |
| Results received | 25 May 2015 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8 | - | - |
|  |  | TSS | 8 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.8 | 6.5-8.5 | - |
|  |  | TSS | 3 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 4 June 2015 |
| --- | --- |
| Results received | 11 June 2015 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8 | - | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.6 | 6.5-8.5 | - |
|  |  | TSS | 12 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |

| Date sampled | 21 July 2015 |
| --- | --- |
| Results received | 28 July 2015 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8 | - | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.3 | 6.5-8.5 | - |
|  |  | TSS | 9 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <2 | 40 | CFU/100mL |
| *Note: EPA Licence variation includes new water quality indicator for Point 4 |

| Date sampled | 6 August 2015 |
| --- | --- |
| Results received | 14 August 2015 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8 | - | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.9 | 6.5-8.5 | - |
|  |  | TSS | 5 | 20 | mg/L |
|  |  | BOD | <1 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |
| *Note: EPA Licence variation includes new water quality indicator for Point 4 |

| Date sampled | 7 September 2015 |
| --- | --- |
| Results received | 15 September 2015 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.8 | - | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.8 | 6.5-8.5 | - |
|  |  | TSS | 8 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |
| *Note: EPA Licence variation includes new water quality indicator for Point 4 |

| Date sampled | 16 October 2015 |
| --- | --- |
| Results received | 26 October 2015 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.08 | - | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | No sample | 6.5-8.5 | - |
|  |  | TSS | No sample | 20 | mg/L |
|  |  | BOD | No sample | 15 | mg/L |
|  |  | *Enterococci | No sample | 40 | CFU/100mL |
| *Note: EPA Licence variation includes new water quality indicator for Point 4 |

| Date sampled | 13 November 2015 |
| --- | --- |
| Results received | 20 November 2015 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.89 | - | - |
|  |  | TSS | <2 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.80 | 6.5-8.5 | - |
|  |  | TSS | <5 | 20 | mg/L |
|  |  | BOD | 4 | 15 | mg/L |
|  |  | *Enterococci | 9 | 40 | CFU/100mL |
| *Note: EPA Licence variation includes new water quality indicator for Point 4 |

| Date sampled | 11 December 2015 |
| --- | --- |
| Results received | 18 December 2015 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.09 | - | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.89 | 6.5-8.5 | - |
|  |  | TSS | 19 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | 23* | 40 | CFU/100mL |
| Note: EPA Licence variation includes new water quality indicator for Point |

| Date sampled | 22 January 2016 |
| --- | --- |
| Results received | 1 February 2016 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.99 | - | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.86 | 6.5-8.5 | - |
|  |  | TSS | <5 | 20 | mg/L |
|  |  | BOD | 4 | 15 | mg/L |
|  |  | *Enterococci | 320 | 40 | CFU/100mL |

| Date sampled | 19 February 2016 |
| --- | --- |
| Results received | 26 February 2016 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.02 | - | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.91 | 6.5-8.5 | - |
|  |  | TSS | 6 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 29 March 2016 |
| --- | --- |
| Results received | 5 April 2016 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.12 | - | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.92 | 6.5-8.5 | - |
|  |  | TSS | <5 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 18 April 2016 |
| --- | --- |
| Results received | 27 April 2016 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.06 | - | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.86 | 6.5-8.5 | - |
|  |  | TSS | 13 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 16 May 2016 |
| --- | --- |
| Results received | 24 May 2016 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.97 | - | - |
|  |  | TSS | 28 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.67 | 6.5-8.5 | - |
|  |  | TSS | 10 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 22 June 2016 |
| --- | --- |
| Results received | 27 June 2016 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.23 | - | - |
|  |  | TSS | 6 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.50 | 6.5-8.5 | - |
|  |  | TSS | 6 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 18 July 2016 |
| --- | --- |
| Results received | 25 July 2016 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.85 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.73 | 6.5-8.5 | - |
|  |  | TSS | 8 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 15 August 2016 |
| --- | --- |
| Results received | 22 August 2016 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.1 | 6.5-8.5 | - |
|  |  | TSS | 9 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.68 | 6.5-8.5 | - |
|  |  | TSS | 8 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 12 September 2016 |
| --- | --- |
| Results received | 20 September 2016 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.98 | 6.5-8.5 | - |
|  |  | TSS | 23 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 8.07 | 6.5-8.5 | - |
|  |  | TSS | 7 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 28 October 2016 |
| --- | --- |
| Results received | 3 November 2016 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.10 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.64 | 6.5-8.5 | - |
|  |  | TSS | 8 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 15 December 2016 |
| --- | --- |
| Results received | 20 December 2016 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.06 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.86 | 6.5-8.5 | - |
|  |  | TSS | 13 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 19 January 2017 |
| --- | --- |
| Results received | 27 January 2017 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.20 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.64 | 6.5-8.5 | - |
|  |  | TSS | <5 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 13 February 2017 |
| --- | --- |
| Results received | 22 February 2017 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.82 | 6.5-8.5 | - |
|  |  | TSS | 16 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.71 | 6.5-8.5 | - |
|  |  | TSS | <5 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 14 March 2017 |
| --- | --- |
| Results received | 21 March 2017 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.02 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.60 | 6.5-8.5 | - |
|  |  | TSS | <5 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 14 April 2017 |
| --- | --- |
| Results received | 21 April 2017 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.25 | 6.5-8.5 | - |
|  |  | TSS | 5 | 50 | mg/L |
|  |  | BOD | 2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.88 | 6.5-8.5 | - |
|  |  | TSS | 14 | 20 | mg/L |
|  |  | BOD | 2 | 15 | mg/L |
|  |  | *Enterococci | 1 | 40 | CFU/100mL |

| Date sampled | 16 May 2017 |
| --- | --- |
| Results received | 23 May 2017 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.2 | 6.5-8.5 | - |
|  |  | TSS | 5 | 50 | mg/L |
|  |  | BOD | 2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.54 | 6.5-8.5 | - |
|  |  | TSS | 10 | 20 | mg/L |
|  |  | BOD | 8 | 15 | mg/L |
|  |  | *Enterococci | 1 | 40 | CFU/100mL |

| Date sampled | 19 June 2017 |
| --- | --- |
| Results received | 26 June 2017 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.1 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.9 | 6.5-8.5 | - |
|  |  | TSS | 7 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 10 July 2017 |
| --- | --- |
| Results received | 17 July 2017 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.08 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | 2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.63 | 6.5-8.5 | - |
|  |  | TSS | 15 | 20 | mg/L |
|  |  | BOD | 4 | 15 | mg/L |
|  |  | *Enterococci | 1 | 40 | CFU/100mL |

| Date sampled | 18 August 2017 |
| --- | --- |
| Results received | 25 August 2017 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.98 | 6.5-8.5 | - |
|  |  | TSS | 5 | 50 | mg/L |
|  |  | BOD | 2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.73 | 6.5-8.5 | - |
|  |  | TSS | 5 | 20 | mg/L |
|  |  | BOD | <5 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 18 September 2017 |
| --- | --- |
| Results received | 25 September 2017 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.95 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | 2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.53 | 6.5-8.5 | - |
|  |  | TSS | 14 | 20 | mg/L |
|  |  | BOD | <5 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 20 October 2017 |
| --- | --- |
| Results received | 26 October 2017 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.78 | 6.5-8.5 | - |
|  |  | TSS | 16 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.76 | 6.5-8.5 | - |
|  |  | TSS | 9 | 20 | mg/L |
|  |  | BOD | 8 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 27 November 2017 |
| --- | --- |
| Results received | 04 December 2017 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.89 | 6.5-8.5 | - |
|  |  | TSS | 8 | 20 | mg/L |
|  |  | BOD | 5 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 20 December 2017 |
| --- | --- |
| Results received | 03 January 2018 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.08 | 6.5-8.5 | - |
|  |  | TSS | 41 | 50 | mg/L |
|  |  | BOD | 2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.99 | 6.5-8.5 | - |
|  |  | TSS | 8 | 20 | mg/L |
|  |  | BOD | 10 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |
| Date sampled | 11 January 2018 |
| Results received | 18 January 2018 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.85 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.72 | 6.5-8.5 | - |
|  |  | TSS | <5 | 20 | mg/L |
|  |  | BOD | 5 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 20 February 2018 |
| --- | --- |
| Results received | 26 February 2018 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.14 | 6.5-8.5 | - |
|  |  | TSS | 43 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.76 | 6.5-8.5 | - |
|  |  | TSS | 15 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 14 March 2018 |
| --- | --- |
| Results received | 21 March 2018 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | No water flow during testing period | 6.5-8.5 | - |
|  |  | TSS |  | 50 | mg/L |
|  |  | BOD |  | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.92 | 6.5-8.5 | - |
|  |  | TSS | 21 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 17 April 2018 |
| --- | --- |
| Results received | 23 April 2018 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.97 | 6.5-8.5 | - |
|  |  | TSS | 18 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.93 | 6.5-8.5 | - |
|  |  | TSS | 13 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 21 May 2018 |
| --- | --- |
| Results received | 28 May 2018 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.04 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.85 | 6.5-8.5 | - |
|  |  | TSS | <5 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 27 June 2018 – Sampling Point 4 10 July 2018 – Sampling Point 2 |
| --- | --- |
| Results received | 04 July 2018 – Sampling Point 4 17 July 2018 – Sampling Point 2 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.05 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.75 | 6.5-8.5 | - |
|  |  | TSS | <15 | 20 | mg/L |
|  |  | BOD | 563 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |
| *Samples had to be taken on separate dates |

| Date sampled | 19 July 2018 |
| --- | --- |
| Results received | 25 July 2018 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.04 | 6.5-8.5 | - |
|  |  | TSS | 13 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.74 | 6.5-8.5 | - |
|  |  | TSS | <8 | 20 | mg/L |
|  |  | BOD | <12 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 21 August 2018 |
| --- | --- |
| Results received | 27 August 2018 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.85 | 6.5-8.5 | - |
|  |  | TSS | 7 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.54 | 6.5-8.5 | - |
|  |  | TSS | 11 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 11 September 2018 |
| --- | --- |
| Results received | 18 September 2018 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.95 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.44 | 6.5-8.5 | - |
|  |  | TSS | 5 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 31 October 2018 |
| --- | --- |
| Results received | 07 November 2018 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.04 | 6.5-8.5 | - |
|  |  | TSS | 43 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.89 | 6.5-8.5 | - |
|  |  | TSS | 130 | 20 | mg/L |
|  |  | BOD | 4 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 21 November 2018 |
| --- | --- |
| Results received | 28 November 2018 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.15 | 6.5-8.5 | - |
|  |  | TSS | 11 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.84 | 6.5-8.5 | - |
|  |  | TSS | 8 | 20 | mg/L |
|  |  | BOD | 3 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 05 December 2018 |
| --- | --- |
| Results received | 12 December 2018 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.13 | 6.5-8.5 | - |
|  |  | TSS | 10 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.86 | 6.5-8.5 | - |
|  |  | TSS | 9 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 23 January 2019 |
| --- | --- |
| Results received | 31 January 2019 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.02 | 6.5-8.5 | - |
|  |  | TSS | 20 | 50 | mg/L |
|  |  | BOD | 2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 8.05 | 6.5-8.5 | - |
|  |  | TSS | 11 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 13 February 2019 |
| --- | --- |
| Results received | 04 March 2019 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.94 | 6.5-8.5 | - |
|  |  | TSS | 23 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.84 | 6.5-8.5 | - |
|  |  | TSS | 8 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 14 March 2019 |
| --- | --- |
| Results received | 21 March 2019 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 8.08 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 8.02 | 6.5-8.5 | - |
|  |  | TSS | 9 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled | 14 April 2019 |
| --- | --- |
| Results received | 15 May 2019 – results were sent to incorrect recipient |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.91 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.91 | 6.5-8.5 | - |
|  |  | TSS | 11 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | 3 | 40 | CFU/100mL |

| Date sampled | 08 May 2019 |
| --- | --- |
| Results received | 15 May 2019 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.85 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | No water flow during testing period | 6.5-8.5 | - |
|  |  | TSS |  | 20 | mg/L |
|  |  | BOD |  | 15 | mg/L |
|  |  | *Enterococci |  | 40 | CFU/100mL |

| Date sampled | 19 June 2019 |
| --- | --- |
| Results received | 28 June 2019 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.76 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.85 | 6.5-8.5 | - |
|  |  | TSS | 20 | 20 | mg/L |
|  |  | BOD | 13 | 15 | mg/L |
|  |  | *Enterococci | 130 | 40 | CFU/100mL |
| *Enterococci level has been reported to the EPA as a pollution incident and corrective action has been taken |

| Date sampled* | 10 July 2019 – Sampling Point 4 18 July 2019 – Sampling Point 2 |
| --- | --- |
| Results received* | 18 July 2019 – Sampling Point 4 25 July 2019 – Sampling Point 2 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.99 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 8.03 | 6.5-8.5 | - |
|  |  | TSS | 9 | 20 | mg/L |
|  |  | BOD | 2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |
| *Samples for outflow 2 were not taken on the 10th of July due to ALS timing issues. Samples were taken separately on the 18th of July |

| Date sampled* | 09 August 2019 – Sampling Point 4 07 August 2019 – Sampling Point 2 |
| --- | --- |
| Results received* | 16 August 2019 – Sampling Point 4 14 August 2019 – Sampling Point 2 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.87 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.20 | 6.5-8.5 | - |
|  |  | TSS | 14 | 20 | mg/L |
|  |  | BOD | 5 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |
| *Samples for outflow 4 were not taken on the 07th of August due to Taronga access issues. Samples were taken separately on the 09th of August. |

| Date sampled* | 03 September 2019 – Sampling Point 2 & 4 |
| --- | --- |
| Results received* | 19 September 2019 – Sampling Point 2 & 4 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.62 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.79 | 6.5-8.5 | - |
|  |  | TSS | 7 | 20 | mg/L |
|  |  | BOD | 2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled* | 03 October 2019 – Sampling Point 2 & 4 |
| --- | --- |
| Results received* | 11 October 2019 – Sampling Point 2 & 4 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.5 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.6 | 6.5-8.5 | - |
|  |  | TSS | <5 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled* | 06 November 2019 – Sampling Point 2 & 4 |
| --- | --- |
| Results received* | 12 November 2019 – Sampling Point 2 & 4 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.91 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 8 | 6.5-8.5 | - |
|  |  | TSS | <5 | 20 | mg/L |
|  |  | BOD | 3 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |

| Date sampled* | 04 December 2019 – Sampling Point 2 & 4 |
| --- | --- |
| Results received* | 15 January 2020 – Sampling Point 2 & 4 |
| Sampling Point | Frequency | Pollutant | Measurement | Limit | Unit |
| 2 | Monthly frequency | pH | 7.83 | 6.5-8.5 | - |
|  |  | TSS | <5 | 50 | mg/L |
|  |  | BOD | <2 | 20 | mg/L |
| 4 | Monthly frequency | pH | 7.79 | 6.5-8.5 | - |
|  |  | TSS | <5 | 20 | mg/L |
|  |  | BOD | <2 | 15 | mg/L |
|  |  | *Enterococci | <1 | 40 | CFU/100mL |